## Common Vent Capacity GAS
|  |  | LINER FINDER - GAS | [8 empty] | LINER FINDER - GAS
| Common Vent Capacity | [9 empty] | Common Vent Capacity
|  | 4 INCH |  |  | 5 INCH |  |  | 5.5 INCH |  |  | 6 INCH |  |  | 7 INCH |  |  | 8 INCH
Chimney | Connector | FAN |  | NAT | FAN |  | NAT | FAN |  | NAT | FAN |  | NAT | FAN |  | NAT | FAN |  | NAT
Height | Type | +FAN | +NAT | +NAT | +FAN | +NAT | +NAT | +FAN | +NAT | +NAT | +FAN | +NAT | +NAT | +FAN | +NAT | +NAT | +FAN | +NAT | +NAT
15 FT | DOUBLE | 100 | 90 | 73 | 156 | 131 | 115 | 191 | 157 | 140 | 226 | 182 | 165 | 342 | 282 | 224 | 445 | 355 | 292
| SINGLE | 97 | 86 | 70 | 151 | 127 | 112 | 186 | 152 | 136 | 220 | 177 | 160 | 333 | 274 | 219 | 435 | 347 | 286
20 FT | DOUBLE | 109 | 98 | 82 | 172 | 146 | 128 | 212 | 175 | 156 | 251 | 204 | 183 | 380 | 315 | 248 | 497 | 399 | 324
| SINGLE | 105 | 94 | 78 | 166 | 142 | 125 | 205 | 170 | 152 | 244 | 198 | 178 | 370 | 306 | 242 | 485 | 390 | 316
25 FT | DOUBLE | 115 | 104 | 88 | 184 | 157 | 138 | 227 | 189 | 168 | 270 | 221 | 198 | 409 | 341 | 268 | 536 | 434 | 350
| SINGLE | 110 | 100 | 84 | 178 | 152 | 134 | 220 | 182 | 163 | 262 | 213 | 192 | 398 | 332 | 260 | 524 | 423 | 342
30 FT | DOUBLE | 122 | 110 | 94 | 195 | 168 | 148 | 242 | 203 | 180 | 289 | 238 | 213 | 438 | 367 | 288 | 576 | 468 | 376
| SINGLE | 116 | 106 | 90 | 189 | 162 | 144 | 234 | 195 | 175 | 280 | 229 | 206 | 426 | 357 | 279 | 562 | 456 | 367
35 FT | DOUBLE | 125 | 113 | 98 | 202 | 175 | 154 | 252 | 212 | 188 | 301 | 249 | 222 | 456 | 385 | 301 | 603 | 492 | 392
| SINGLE | 119 | 108 | 93 | 195 | 168 | 150 | 243 | 203 | 182 | 291 | 239 | 213 | 444 | 373 | 291 | 588 | 479 | 382
40 FT | DOUBLE | 128 | 116 | 101 | 209 | 182 | 160 | 261 | 221 | 195 | 313 | 260 | 230 | 475 | 402 | 313 | 630 | 516 | 408
| SINGLE | 122 | 111 | 96 | 202 | 174 | 155 | 252 | 212 | 188 | 302 | 249 | 221 | 462 | 390 | 304 | 614 | 502 | 398
45 FT | DOUBLE | 131 | 119 | 104 | 216 | 188 | 165 | 271 | 230 | 202 | 325 | 271 | 239 | 494 | 420 | 326 | 656 | 541 | 424
| SINGLE | 124 | 113 | 99 | 208 | 180 | 161 | 261 | 220 | 195 | 314 | 259 | 229 | 480 | 407 | 316 | 640 | 526 | 413
50 FT | DOUBLE | 134 | 122 | 107 | 223 | 195 | 171 | 280 | 239 | 210 | 337 | 282 | 248 | 513 | 438 | 338 | 683 | 565 | 440
| SINGLE | 127 | 116 | 102 | 214 | 186 | 166 | 270 | 228 | 202 | 325 | 270 | 237 | 498 | 423 | 328 | 666 | 549 | 428
Instructions:
1. Set lateral feet at height
2. Read BTU input maximum in thousands at Z-Flex diameter, for double wall
(Insul-Vent, "B" vent) or single wall connector type.
3. USE FOR SIZING ONLY Z-FLEX LINER KITS
All data from National Fuel Gas Code (NFPA 54). All capacities have been reduced 20% as required for corrugated liners.

## Common Vent Capacity OIL
[5 empty] | LINER FINDER - OIL | [6 empty] | LINER FINDER - OIL
|  | Appliance Efficiency | [7 empty] | Measurements in Gal./HR.
|  | 80% |  |  | 5 INCH |  |  | 84% |  |  | 86% |  |  | 88%
Chimney | Lateral | Diameters |  |  | Diameters |  |  | Diameters |  |  | Diameters |  |  | Diameters
Height | Feet | 4 | 5 | 6 | 4 | 5 | 6 | 4 | 5 | 6 | 4 | 5 | 6 | 4 | 5 | 6
10 FT | 4 FT | .25 - .65 | .25 - 1.0 | .25 - 1.75 | .25 - .5 | .25 - 1.0 | .4 - 1.5 | .25 - .5 | .25 - .85 | .4 - 1.5 | .25 - .5 | .4 - .85 | .4 - 1.25 | 0.25 | .4 - .65 | .5 - 1.0
| 10 FT | .25 - .65 | .25 - 1.0 | .4 - 1.5 | .25 - .5 | .25 - .85 | .4 - 1.5 | .25 - .4 | .25 - .85 | .4 - 1.25 | 0.25 | .4 - .75 | .4 - 1.25 | NR | NR | .4 - .75
15 FT | 4 FT | .25 - .75 | .4 - 1.25 | .4 - 2.0 | .25 - .65 | .4 - 1.25 | .4 - 1.75 | .25 - .65 | .4 - 1.0 | .5 - 1.75 | .4 - .5 | .4 - 1.0 | .5 - 1.5 | 0.4 | .4 - .75 | .65 - 1.25
| 10 FT | .25 - .75 | .4 - 1.25 | .5 - 2.0 | .25 - .65 | .4 - 1.0 | .4 - 1.75 | .4 - .5 | .4 - 1.0 | .65 - 1.5 | .4 - .5 | .4 - .85 | .5 - 1.25 | 0.4 | .4 - .75 | .5 - 1.0
20 FT | 4 FT | .4 - .85 | .4 - 1.5 | .4 - 2.25 | .4 - .75 | .4 - 1.25 | .5 - 2.0 | .4 - .65 | .5 - 1.25 | .65 - 1.75 | .4 - .5 | .5 - 1.0 | .65 - 1.75 | 0.4 | .5 - .85 | .65 - 1.5
| 10 FT | .4 - .75 | .4 - 1.25 | .4 - 2.0 | .4 - .75 | .4 - 1.25 | .5 - 2.0 | .4 - .5 | .5 - 1.0 | .65 - 1.75 | .4 - .5 | .5 - 1.0 | .65 - 1.5 | .4 - .5 | .65 - .85 | .65 - 1.25
25 FT | 4 FT | .4 - .85 | .4 - 1.5 | .4 - 2.25 | .4 - .75 | .5 - 1.5 | .5 - 2.25 | .4 - .75 | .5 - 1.25 | .65 - 2.0 | .4 - .5 | .5 - 1.0 | .75 - 1.75 | 0.5 | .65 - 1.0 | .75 - 1.5
| 10 FT | .4 - .85 | .5 - 1.5 | .65 - 2.25 | .4 - .75 | .5 - 1.25 | .65 - 2.0 | .4 - .65 | .5 - 1.25 | .65 - 2.0 | .4 - 5 | .65 - 1.0 | .75 - 1.75 | 0.5 | .65 - .85 | .85 - 1.25
35 FT | 4 FT | .4 - .85 | .5 - 1.75 | .5 - 2.25 | .5 - .85 | .65 - 1.5 | .65 - 2.25 | .5 - .75 | .65 - 1.5 | .85 - 2.25 | .5 - .65 | .65 - 1.25 | .85 - 2.0 | 0.5 | .75 - 1.0 | 1.0 - 1.75
| 10 FT | 04 - .85 | .65 - 1.5 | .65 - 2.25 | .5 - .85 | .65 - 1.5 | .75 - 2.25 | .5 - .75 | .65-1.25 | .85 - 2.25 | .5 - .65 | .65 - 1.25 | .85 - 2.0 | 0.5 | .75 - 1.0 | 1.0 - 1.5
45 FT | 4 FT | .5 - 1.5 | .65 - 1.75 | .65 - 2.25 | .5 - .85 | .75 - 1.5 | .75 - 2.25 | .65 - .75 | .75 - 1.5 | 1.0 - 2.25 | .65 - .75 | .75 - 1.25 | 1.0 - 2.25 | 0.65 | .85 - 1.0 | 1.25 -1.75
| 10 FT | .5 - .85 | .65 - 1.75 | .65 - 2.25 | .5 - .85 | .75 - 1.5 | .85 - 2.25 | .65 - .75 | .75 - 1.5 | 1.0 - 2.25 | .65 - .75 | .85 - 1.25 | 1.0 - 2.0 | 0.65 | .85 - 1.0 | 1.25 -1.75
Instructions:
1. Set lateral feet at height
2. Read correct liner diameter at efficiency and your firing rate
3. USE FOR SIZING ONLY Z-FLEX LINER KITS
All data from NFPA 31 (2001)

## Liner Finder GAS
LINER FINDER - GAS
Single Category I Appliance
|  |  | 3 INCH |  |  | 4 INCH |  |  | 5 INCH |  |  | 5.5 INCH |  |  | 6 INCH |  |  | 7 INCH |  |  | 8 INCH
Chimney | Connector | LAT | FAN |  | NAT | FAN |  | NAT | FAN |  | NAT | FAN |  | NAT | FAN |  | NAT | FAN |  | NAT | FAN |  | NAT
Height | Type |  | MIN | MAX | MAX | MIN | MAX | MAX | MIN | MAX | MAX | MIN | MAX | MAX | MIN | MAX | MAX | MIN | MAX | MAX | MIN | MAX | MAX
|  | 2 | 9 | 55 | 38 | 12 | 109 | 74 | 16 | 181 | 120 | 17 | 226 | 150 | 18 | 271 | 180 | 30 | 380 | 253 | 36 | 506 | 331
|  | 5 | 18 | 52 | 36 | 24 | 104 | 70 | 31 | 175 | 114 | 35 | 220 | 144 | 39 | 264 | 174 | 51 | 370 | 240 | 61 | 496 | 322
| Double | 10 | 23 | 47 | 33 | 32 | 97 | 66 | 41 | 165 | 108 | 46 | 208 | 137 | 51 | 252 | 166 | 67 | 356 | 230 | 79 | 480 | 309
|  | 15 | 28 | 42 | 30 | 38 | 90 | 61 | 49 | 156 | 102 | 55 | 198 | 130 | 61 | 241 | 158 | 78 | 343 | 220 | 92 | 464 | 298
15 FT |  | 20 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR
|  | 2 | 30 | 55 | 38 | 46 | 109 | 74 | 64 | 180 | 119 | 78 | 225 | 149 | 92 | 270 | 179 | 118 | 378 | 251 | 150 | 505 | 330
|  | 5 | 41 | 50 | 35 | 60 | 102 | 69 | 82 | 173 | 112 | 98 | 217 | 143 | 115 | 261 | 174 | 146 | 367 | 238 | 185 | 493 | 320
| Single | 10 | NR | NR | 31 | 76 | 93 | 63 | 102 | 161 | 105 | 124 | 204 | 134 | 146 | 246 | 162 | 182 | 350 | 227 | 227 | 474 | 305
|  | 15 | NR | NR | NR | NR | NR | 58 | 126 | 149 | 99 | 151 | 190 | 126 | 176 | 232 | 154 | 218 | 334 | 215 | 267 | 454 | 294
|  | 20 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR
|  | 2 | 8 | 60 | 41 | 11 | 119 | 80 | 14 | 200 | 133 | 15 | 251 | 166 | 16 | 302 | 199 | 26 | 425 | 277 | 33 | 569 | 376
|  | 5 | 17 | 57 | 38 | 23 | 114 | 77 | 30 | 194 | 128 | 34 | 244 | 160 | 38 | 294 | 193 | 50 | 415 | 270 | 58 | 558 | 368
| Double | 10 | 22 | 51 | 35 | 30 | 106 | 71 | 40 | 183 | 120 | 45 | 232 | 151 | 50 | 281 | 182 | 65 | 399 | 257 | 76 | 540 | 354
|  | 15 | 27 | 46 | 32 | 37 | 99 | 67 | 47 | 174 | 114 | 53 | 222 | 144 | 58 | 270 | 174 | 75 | 358 | 246 | 89 | 523 | 342
20 FT |  | 20 | 38 | 42 | 28 | 44 | 93 | 62 | 55 | 165 | 107 | 61 | 211 | 136 | 67 | 258 | 165 | 86 | 371 | 236 | 100 | 507 | 328
|  | 2 | 30 | 59 | 40 | 45 | 118 | 79 | 62 | 198 | 132 | 76 | 249 | 165 | 90 | 300 | 198 | 115 | 422 | 275 | 146 | 566 | 374
|  | 5 | 40 | 54 | 38 | 58 | 112 | 75 | 80 | 191 | 126 | 96 | 241 | 159 | 113 | 290 | 191 | 142 | 411 | 267 | 179 | 554 | 366
| Single | 10 | NR | NR | 33 | 74 | 103 | 69 | 100 | 178 | 117 | 121 | 227 | 148 | 142 | 275 | 179 | 178 | 393 | 253 | 222 | 533 | 350
|  | 15 | NR | NR | NR | NR | NR | 64 | 124 | 166 | 109 | 148 | 213 | 138 | 173 | 260 | 168 | 211 | 375 | 241 | 260 | 512 | 335
|  | 20 | NR | NR | NR | NR | NR | NR | 149 | 154 | 101 | 176 | 199 | 129 | 203 | 245 | 157 | 247 | 358 | 228 | 299 | 493 | 320
|  | 2 | 8 | 62 | 43 | 11 | 126 | 85 | 13 | 213 | 140 | 14 | 268 | 176 | 15 | 324 | 212 | 24 | 458 | 296 | 30 | 615 | 402
|  | 5 | 17 | 59 | 41 | 23 | 121 | 82 | 30 | 207 | 134 | 33 | 261 | 170 | 37 | 315 | 206 | 48 | 448 | 289 | 57 | 603 | 394
| Double | 10 | 22 | 54 | 38 | 30 | 113 | 76 | 39 | 196 | 128 | 44 | 249 | 162 | 48 | 302 | 196 | 63 | 432 | 277 | 74 | 585 | 380
|  | 15 | 27 | 49 | NR | 36 | 106 | 72 | 46 | 186 | 122 | 52 | 238 | 154 | 57 | 290 | 186 | 74 | 416 | 266 | 86 | 568 | 367
25 FT |  | 20 | 42 | 44 | NR | 43 | 99 | 67 | 54 | 177 | 115 | 60 | 228 | 146 | 66 | 278 | 177 | 84 | 402 | 255 | 98 | 551 | 353
|  | 2 | 30 | 62 | 42 | 44 | 125 | 84 | 62 | 212 | 139 | 75 | 267 | 175 | 89 | 322 | 211 | 113 | 455 | 294 | 143 | 612 | 400
|  | 5 | 40 | 57 | 40 | 58 | 119 | 80 | 79 | 204 | 132 | 95 | 258 | 168 | 111 | 312 | 204 | 140 | 444 | 286 | 176 | 599 | 391
| Single | 10 | NR | NR | NR | 74 | 109 | 74 | 99 | 191 | 126 | 119 | 244 | 159 | 139 | 296 | 192 | 174 | 424 | 273 | 217 | 577 | 375
|  | 15 | NR | NR | NR | NR | NR | NR | 122 | 179 | 117 | 146 | 230 | 149 | 170 | 281 | 181 | 208 | 406 | 260 | 255 | 556 | 360
|  | 20 | NR | NR | NR | NR | NR | NR | 147 | 166 | NR | 173 | 216 | NR | 200 | 265 | 170 | 243 | 389 | 247 | 294 | 536 | 344
|  | 2 | 7 | 65 | 45 | 10 | 133 | 90 | 11 | 226 | 148 | 13 | 286 | 186 | 14 | 346 | 224 | 22 | 490 | 315 | 26 | 661 | 428
|  | 5 | 17 | 62 | 43 | 22 | 128 | 86 | 29 | 220 | 141 | 32 | 278 | 180 | 36 | 337 | 218 | 46 | 480 | 308 | 55 | 649 | 419
| Double | 10 | 22 | 56 | 40 | 30 | 120 | 82 | 38 | 210 | 137 | 43 | 267 | 173 | 47 | 324 | 209 | 62 | 464 | 297 | 73 | 630 | 406
|  | 15 | 26 | 51 | NR | 35 | 113 | 77 | 46 | 199 | 130 | 51 | 255 | 165 | 56 | 311 | 199 | 72 | 448 | 286 | 84 | 612 | 392
30 FT |  | 20 | 45 | 46 | NR | 42 | 106 | 72 | 53 | 190 | 123 | 58 | 244 | 156 | 64 | 299 | 190 | 82 | 434 | 274 | 95 | 594 | 378
|  | 2 | 30 | 64 | 45 | 44 | 131 | 89 | 61 | 225 | 146 | 74 | 284 | 185 | 87 | 343 | 223 | 111 | 488 | 314 | 140 | 658 | 426
|  | 5 | 39 | 59 | 42 | 58 | 126 | 85 | 78 | 217 | 138 | 94 | 275 | 178 | 109 | 334 | 217 | 137 | 476 | 306 | 172 | 645 | 417
| Single | 10 | NR | NR | NR | 73 | 115 | 78 | 98 | 204 | 134 | 117 | 261 | 170 | 137 | 318 | 206 | 170 | 456 | 294 | 212 | 622 | 401
|  | 15 | NR | NR | NR | 92 | 105 | NR | 121 | 191 | 126 | 144 | 246 | 160 | 166 | 302 | 194 | 204 | 438 | 279 | 250 | 600 | 385
|  | 20 | NR | NR | NR | NR | NR | NR | 145 | 178 | NR | 171 | 232 | NR | 197 | 286 | 182 | 238 | 419 | 266 | 288 | 578 | 369
|  | 2 | 7 | 66 | 46 | 10 | 136 | 92 | 11 | 234 | 152 | 13 | 296 | 192 | 14 | 359 | 231 | 21 | 511 | 325 | 25 | 691 | 444
|  | 5 | 17 | 63 | NR | 22 | 131 | 89 | 29 | 227 | 146 | 32 | 289 | 186 | 36 | 350 | 225 | 46 | 500 | 319 | 54 | 679 | 435
| Double | 10 | 21 | 57 | NR | 29 | 124 | 84 | 38 | 217 | 141 | 42 | 277 | 178 | 47 | 337 | 216 | 61 | 484 | 308 | 72 | 660 | 422
|  | 15 | 32 | 52 | NR | 35 | 116 | NR | 45 | 207 | 134 | 50 | 266 | 170 | 55 | 324 | 207 | 71 | 468 | 297 | 83 | 641 | 408
35 FT |  | 20 | NR | NR | NR | 42 | 109 | NR | 52 | 197 | 126 | 58 | 255 | 162 | 63 | 312 | 198 | 81 | 454 | 286 | 94 | 623 | 395
|  | 2 | 29 | 65 | 46 | 44 | 135 | 91 | 60 | 232 | 151 | 73 | 294 | 190 | 86 | 356 | 230 | 110 | 508 | 324 | 139 | 688 | 442
|  | 5 | 39 | 60 | NR | 57 | 129 | 87 | 78 | 224 | 143 | 93 | 285 | 184 | 108 | 347 | 224 | 135 | 496 | 316 | 170 | 674 | 433
| Single | 10 | NR | NR | NR | 72 | 118 | NR | 97 | 211 | 138 | 116 | 271 | 175 | 135 | 330 | 213 | 168 | 476 | 304 | 210 | 651 | 417
|  | 15 | NR | NR | NR | 91 | 108 | NR | 120 | 198 | 129 | 142 | 256 | 165 | 165 | 314 | 201 | 202 | 457 | 290 | 247 | 629 | 401
|  | 20 | NR | NR | NR | NR | NR | NR | 144 | 185 | NR | 169 | 242 | NR | 195 | 298 | 190 | 236 | 439 | 278 | 285 | 607 | 385
|  | 2 | 7 | 67 | 47 | 10 | 140 | 94 | 11 | 241 | 156 | 12 | 306 | 197 | 13 | 372 | 238 | 20 | 531 | 336 | 24 | 720 | 460
|  | 5 | 16 | 64 | NR | 22 | 135 | 91 | 28 | 235 | 150 | 32 | 299 | 191 | 35 | 363 | 232 | 45 | 521 | 329 | 54 | 708 | 452
| Double | 10 | 21 | 58 | NR | 29 | 127 | 86 | 37 | 224 | 144 | 42 | 287 | 184 | 46 | 350 | 224 | 60 | 504 | 319 | 71 | 689 | 438
|  | 15 | 37 | 54 | NR | 34 | 120 | NR | 44 | 214 | 137 | 49 | 276 | 176 | 54 | 338 | 215 | 70 | 489 | 308 | 82 | 670 | 425
40 FT |  | 20 | NR | NR | NR | 41 | 112 | NR | 52 | 205 | 129 | 57 | 265 | 168 | 62 | 326 | 206 | 80 | 474 | 298 | 93 | 652 | 412
|  | 2 | 29 | 66 | 47 | 43 | 138 | 93 | 60 | 240 | 155 | 72 | 305 | 196 | 85 | 370 | 236 | 109 | 529 | 334 | 137 | 718 | 458
|  | 5 | 39 | 62 | NR | 57 | 132 | 89 | 77 | 232 | 148 | 92 | 296 | 189 | 107 | 360 | 230 | 134 | 516 | 327 | 168 | 704 | 449
| Single | 10 | NR | NR | NR | 72 | 122 | NR | 96 | 219 | 142 | 115 | 281 | 181 | 133 | 343 | 220 | 166 | 496 | 315 | 207 | 680 | 434
|  | 15 | NR | NR | NR | 91 | 112 | NR | 118 | 206 | 132 | 141 | 266 | 171 | 163 | 327 | 209 | 200 | 477 | 302 | 244 | 658 | 417
|  | 20 | NR | NR | NR | NR | NR | NR | 143 | 192 | NR | 168 | 251 | NR | 193 | 311 | 198 | 233 | 458 | 289 | 282 | 636 | 402
|  | 2 | 7 | 68 | 48 | 9 | 143 | 96 | 11 | 249 | 161 | 12 | 317 | 203 | 13 | 385 | 244 | 19 | 552 | 346 | 22 | 750 | 476
|  | 5 | 16 | 65 | NR | 22 | 138 | 93 | 28 | 242 | 155 | 32 | 309 | 197 | 35 | 376 | 239 | 45 | 541 | 340 | 53 | 738 | 468
| Double | 10 | 21 | 60 | NR | 28 | 131 | 89 | 37 | 232 | 148 | 41 | 298 | 190 | 45 | 364 | 231 | 59 | 525 | 330 | 70 | 719 | 455
|  | 15 | 42 | 55 | NR | 34 | 123 | NR | 44 | 222 | 141 | 49 | 286 | 182 | 54 | 351 | 223 | 69 | 509 | 319 | 81 | 700 | 441
45 FT |  | 20 | NR | NR | NR | 41 | 116 | NR | 51 | 212 | 132 | 56 | 276 | 173 | 62 | 339 | 214 | 79 | 494 | 309 | 92 | 681 | 428
|  | 2 | 29 | 66 | 48 | 43 | 141 | 95 | 59 | 247 | 160 | 72 | 315 | 201 | 84 | 383 | 243 | 108 | 549 | 344 | 136 | 747 | 474
|  | 5 | 39 | 63 | NR | 56 | 136 | 91 | 76 | 239 | 153 | 91 | 306 | 195 | 106 | 373 | 237 | 133 | 537 | 337 | 165 | 733 | 465
| Single | 10 | NR | NR | NR | 72 | 125 | NR | 95 | 226 | 145 | 113 | 291 | 186 | 131 | 356 | 227 | 164 | 517 | 325 | 205 | 709 | 450
|  | 15 | NR | NR | NR | 90 | 115 | NR | 117 | 213 | 136 | 139 | 276 | 176 | 161 | 340 | 216 | 197 | 497 | 313 | 242 | 686 | 433
|  | 20 | NR | NR | NR | NR | NR | NR | 142 | 199 | NR | 166 | 261 | NR | 191 | 323 | 206 | 231 | 478 | 300 | 279 | 664 | 418
|  | 2 | 6 | 69 | 49 | 9 | 146 | 98 | 11 | 256 | 165 | 12 | 327 | 208 | 12 | 398 | 251 | 18 | 572 | 356 | 21 | 780 | 492
|  | 5 | 16 | 66 | NR | 22 | 142 | 95 | 28 | 250 | 160 | 31 | 320 | 203 | 34 | 390 | 246 | 44 | 562 | 350 | 52 | 768 | 484
| Double | 10 | 21 | 61 | NR | 28 | 134 | 91 | 36 | 239 | 152 | 40 | 308 | 195 | 45 | 377 | 238 | 58 | 545 | 341 | 69 | 748 | 471
|  | 15 | 47 | 56 | NR | 34 | 126 | NR | 43 | 230 | 144 | 48 | 297 | 187 | 53 | 364 | 230 | 68 | 530 | 330 | 80 | 729 | 458
50 FT |  | 20 | NR | NR | NR | 40 | 119 | NR | 50 | 220 | 135 | 56 | 286 | 179 | 61 | 352 | 222 | 78 | 514 | 321 | 90 | 710 | 445
|  | 2 | 29 | 67 | 49 | 42 | 145 | 97 | 58 | 254 | 164 | 71 | 325 | 207 | 83 | 396 | 250 | 106 | 570 | 354 | 134 | 777 | 490
|  | 5 | 38 | 64 | NR | 56 | 139 | 94 | 75 | 246 | 158 | 90 | 316 | 201 | 105 | 386 | 244 | 131 | 557 | 348 | 163 | 762 | 482
| Single | 10 | NR | NR | NR | 71 | 128 | NR | 94 | 234 | 149 | 112 | 301 | 191 | 130 | 369 | 234 | 162 | 537 | 336 | 202 | 738 | 466
|  | 15 | NR | NR | NR | 90 | 118 | NR | 116 | 220 | 139 | 138 | 286 | 182 | 159 | 353 | 224 | 195 | 517 | 324 | 239 | 715 | 450
|  | 20 | NR | NR | NR | NR | NR | NR | 141 | 206 | NR | 165 | 271 | NR | 189 | 336 | 214 | 228 | 498 | 311 | 276 | 693 | 434